Section 08373 Architectural Specifications

UltraSecure 3000 High Speed Metal Door

SECTION 08373

HIGH SPEED ROLLING DOORS

PART 1 – GENERAL

  - SECTION INCLUDES

  - Work described in this section includes manufacture, delivery and installation of high speed rolling doors, control devices and actuator systems.

  - Related work is described in other sections:

- Field painting

- Electrical connections

  - RELATED SECTIONS

  - Field painting

  - Electrical connections

  - REFERENCES

- American Society for Testing and Materials (ASTM)

- National Electrical Manufacturer's Association (NEMA)

- Underwriters Laboratories, Inc. (CUL)

  - SYSTEM DESCRIPTION

- Electrical Motor operated unit with manual override in case of power failure.

  - SUBMITTALS

- Submit the following:

  - Shop Drawings:  Indicate pertinent dimensioning, anchorage methods, hardware locations and installation details.

  - Product Data:  Provide general construction, component connections and details, electrical equipment and operation instructions.

  - Samples:  Submit color samples of door panels for selection by owner.

  - Manufacturer's Installation:  Indicate installation sequence and procedures, adjustment and alignment procedures.

  - REGULARTORY REQUIREMENTS

- Electrical components UL listed.

- Electrical enclosure NEMA approved.

  - PERFORMANCE REQUIREMENTS

- Wind Loading: High speed rolling door to withstand a windload condition of 21 lbs. per sq ft (90 mph) when closed for door widths <=16 ft.

1.08   QUALITY ASSURANCE

- Furnish high-speed roll doors and all components and accessories by one manufacturer.

1.09   FIELD MEASUREMENTS

- Verify field measurements are as indicated on shop drawings.

1.10   COORDINATION

- Coordinate the work with installation of electric power and locations and sizes of conduit.

1.11   WARRANTY

- One year warranty covering material and workmanship defects on mechanical and electrical components.

- One year labor warranty.

PART 2 – PRODUCTS

2.01   PRODUCTS

- Albany Door Systems UltraSecure 3000 high speed door.

- No substitutions permitted.

  - MATERIALS

- Door Panel:

  - Anodized aluminum slats with highly durable EPDM rubber weather seal between slats.

  - Hingeless slat connection allows door to stay in service during slat replacement.

  - Characteristics of the slats

    - Double walled anodized extruded aluminum

    - Cross section: 4.92” X  0.79”

  - Each individual slat can be easily removed and replaced within the space of the overall door.

  - Slats shall be designed with an overlap, which prevents water from collecting on rubber weather seal (exterior side).

- Door Roll:

  - Fabricate 4.25" diameter, steel tube from 11 gauge steel complying with ASTM A513.

  - Drum tube deflection shall not exceed 0.01" per foot and shall not exceed 0.14" over the entire length.

  - To incorporate disc drive system for frictionless winding of door curtain.

  - Door slats shall not contact one another when door is rolled up in open position.

- Counterbalanced System:

  - Internally mounted counterbalance system shall utilize extension springs along with a belt and pulley mechanism. Torsion spring shall not be located within the top roll barrel.

  - Redundant springs keep the door operating should a primary spring break.

  - Durable machined aluminum pulleys.  Each pulley shall contain two permanently sealed and lubricated ball bearings.

  - Provide manufacturer's standard factory 1.18” nylon belting.

  - Side frames to include disengagement lever which allows door to be manually opened in the event of a power failure.

- Drive System:

  - Minimum 1.5HP in line hollow shaft helical-bevel drive with three phase variable speed AC drive.

  - Gearmotor must be accessible while door is in any position.

- Control Panel:

  - UltraSmart controller housed in a NEMA 4 / 12 enclosure.

  - Control Panel must be provided with fusible rotary disconnect mounted on the control panel.  No exceptions.

  - Controls must include a variable frequency drive system capable of infinitely variable speed control in both the up and down directions.  Fused 24V AC power for the door controller and optional activators.

  - All interior control panel components must be touch-safe (protected from high voltage when control panel door is open).  NO EXPOSED HIGH VOLTAGE CONTACTS.

  - All door operational parameters must be set on the outside face of the control panel.  No fixed or rotary limit switches.  No exceptions.

  - Controller comes with factory set parameters, a two line display that shows functional information during normal operation and will advise if maintenance is required for abnormal situations.

  - Controller and panel must be fully modular.  Separate modules for activation, safety, drive, controls, operation and all other options.  Must be expandable to accommodate additional modules for desired inputs and outputs.

  - Controls must be fully self diagnostic.

  - Door must be provided with an absolute encoder.

  - Door to be fully wireless. No coil cords mounted in the side columns. Safety edge and activation must be read and monitored wirelessly on the front of the controls

- Side Frame:

  - Frame: 11 gauge galvanized steel sections, which includes the lateral structural frame assembly with a bolt on cover, to guide the door panel in its upward and downward movement.

  - UHMW lined tracks for smooth panel movement

- Safety Features:

  - Door to be provided with CarGuard Safety Light Curtain System.

  - Light curtain must be located inside of the side frame material and cover area up to a height of no less than six feet.

  - Light curtain system must have a minimum of 96 infrared thru-beam optical sensors.

  - Control panel must indicate in written visible English each time the light curtain is broken.

  - Door must be provided with a BacOut Safety System allowing the door panel to open manually without the use of hand cranks in the event of a power outage.  Counter-balance design must allow the door to be opened in event of power failure.

  - Door to be provided with failsafe electric safety edge.  Door controller must indicate if the safety edge is not operable.

  - Door must be fully wireless. No coil cords allowed

- Speed:

  - Door to operate at a variable speed up to 80" per second in the up direction.  Door must operate at a variable speed in the down direction.

- All components furnished by factory.

PART 3 – EXECUTION

3.01   EXAMINATION

- Verify that opening sizes, tolerances and conditions are acceptable.

3.02   INSTALLATION

- Install door assembly in accordance with manufacturer's instructions.

- Use anchorage devices to securely fasten assembly to wall constructions and building framing without distortion or stress.

- Fit and align assembly including hardware; level to plumb to provide smooth operation.

- Coordinate installation of electrical service.  Complete wiring from disconnect to unit components.

3.03   ADJUSTING

- Adjust door and operating assemblies.

- Test and adjust door, if necessary, for proper operations.

3.04   CLEANING

- Clean door and components.

END OF SECTION